## Calculator Dashboard
POWER FACTOR & CAPACITOR BANK DIAGNOSTIC CALCULATOR
Bill Based PF Correction + Existing Capacitor Bank + Solar CT Diagnostic + Transformer Shutdown
BILL DATA |  | CALCULATED CURRENT PF | 0.82911
Energy - Peak | 368000
Energy - Off Peak | 53243.311 | DESIRED PF | 0.95
Reactive Energy - Peak | 254000
Reactive Energy - Off Peak | 30057.613 | Required Capacitor Capacity | 237.5
MDI (kW) | 689.662
Note:This calculation and recommendation are based on the average monthly bill data and the current PF calculated from the information provided. Actual site conditions may differ. For further consultation or a detailed assessment, please contact our PFI Team at power.factor@ke.com.pk
RECOMMENDED CAPACITOR BANK
100 kVAR | 50 kVAR | 25 kVAR | 12.5 kVAR
2 | 0 | 1 | 1
7.5 kVAR | 5 kVAR | 2.5 kVAR | 3.5 kVAR
0 | 0 | 0 | 1
TOTAL RECOMMENDED BANK |  | STEP CONFIGURATION
237.5 |  | 2 × 100 kVAR, 1 × 25 kVAR, 1 × 12.5 kVAR, 1 × 2.5 kVAR
EXISTING CAPACITOR BANK
Do you already have a capacitor bank? |  | Yes
100 kVAR | 50 kVAR | 25 kVAR | 12.5 kVAR
2 | 1 | 1 | 1
7.5 kVAR | 5 kVAR | 3.5 kVAR | 2.5 kVAR
2 | 1 | 1 | 1
INSTALLED CAPACITY |  | BANK VS REQUIRED
313.5 |  | Installed bank is theoretically sufficient
TRANSFORMER ENERGIZED / FACTORY SHUTDOWN
Factory Load (kW) | Transformer Rating (kVA) | Existing Capacitor Bank? | Yes / No
0 | 750 | Est. No-load kVAR | 9.2879
RECOMMENDED NO-LOAD COMPENSATION
12.5
Engineering estimates are indicative. Final capacitor-bank selection, CT location, and transformer no load compensation should be verified against actual site measurements, equipment data and the applicable tariff/metering arrangement.

## Engineering Calculations
ENGINEERING CALCULATIONS
Bill Inputs
Energy - Peak | 368000
Energy - Off Peak | 53243.311
Reactive Energy - Peak | 254000
Reactive Energy - Off Peak | 30057.613
MDI (kW) | 689.662
Desired PF | 0.95
Calculated Current PF | 0.82911
Total Active Energy (kWh) | 421243.311
Total Reactive Energy (kVARh) | 284057.613
Target Reactive Energy (kVARh) — internal calculation | 138455.9807
Required Reactive Energy Compensation (kVARh) — internal calculation | 145601.6323
Calculated Capacitor Requirement (kVAR) using MDI | 238.3798
100 kVAR Steps | 2 | Required | Recommended
50 kVAR Steps | 0 | kVAR | kVAR
25 kVAR Steps | 1 | 238.3798 | 237.5
12.5 kVAR Steps | 1
7.5 kVAR Steps | 0
5 kVAR Steps | 0
3.5 kVAR Steps | 0
2.5 kVAR Steps | 1
Required Capacitor Capacity (kVAR) | 237.5
Step Configuration | 2 × 100 kVAR, 1 × 25 kVAR, 1 × 12.5 kVAR, 1 × 2.5 kVAR
Existing 100 kVAR qty | 2
Existing 50 kVAR qty | 1
Existing 25 kVAR qty | 1
Existing 12.5 kVAR qty | 1
Existing 7.5 kVAR qty | 2
Existing 5 kVAR qty | 1
Existing 3.5 kVAR qty | 1
Existing 2.5 kVAR qty | 1
Installed Capacity (kVAR) | 313.5
Bank Adequacy | Installed bank is theoretically sufficient
Solar PV | #REF!
CT Location | #REF!
Solar / CT Diagnostic | #REF!
Factory Load | 0
Transformer Rating | 750
Estimated Transformer No-load kVA | 9.375
Estimated Transformer No-load kW | 1.275
Estimated Transformer No-load kVAR | 9.2879
Recommended No-load Compensation (kVAR) | 12.5
Recommended Step | 12.5 kVAR

## Assumptions & Notes (hidden)
ASSUMPTIONS & NOTES
PFC formula | Qc = P × [tan(cos⁻¹(PFexisting)) − tan(cos⁻¹(PFdesired))].
Bill PF | Billing-period PF is derived from total active and reactive energy: PF = kWh / √(kWh² + kVARh²).
Bill terminology | Customer inputs use the bill wording: Energy - Peak, Energy - Off Peak, Reactive Energy - Peak, Reactive Energy - Off Peak, MDI (kW).
Capacitor sizing | MDI and calculated billing PF are used to estimate a practical capacitor-bank kVAR requirement.
Existing bank | Installed step quantities are compared with the estimated requirement; adequacy does not prove that every capacitor step is healthy.
Solar CT diagnostic | CT location must be evaluated against the actual single-line diagram, PCC and controller measurement philosophy. The calculator flags cases for verification; it does not certify an installation.
Transformer no-load | Typical rating-band assumptions are used because nameplate/test-certificate no-load data are often unavailable.
Engineering caution | Final design should be verified with site measurements, manufacturer data, protection/metering configuration and applicable tariff requirements.